## Bowral Website Report
BOWRAL SEWAGE TREATMENT SYSTEM
LICENCE NUMBER 1749
Licencing Period 1 May 2024 - 30 April 2025
FINAL EFFLUENT MONITORING FORTNIGHTLY TEST RESULTS (POINT 1)
SAMPLE ANALYSIS DATE |  |  |  | BOD | TSS | Ammonia | Total N | Total P | pH | Faecal coliforms | *Oil & Grease
Taken | Received | Reviewed by | Published | (mg/L) | (mg/L) | (mg/L) N | TKN+NOx (mg/L) | (mg/L) P | pH units | (CFU/100mL) | (mg/L)
2024-05-14 | 2024-05-23 | EH | 2024-06-04 | 2 | 9 | 0.77 | 3.21 | 0.22 | 7.2 | 67 | NA
2024-05-28 | 2024-06-06 | WM | 2024-06-14 | 4 | 9 | 1.06 | 7.26 | 0.222 | 7.3 | 190 | NA
2024-06-11 | 2024-06-22 | EH | 2024-06-28 | 5 | 8 | 1.97 | 6.42 | 0.377 | 7.1 | 1 | NA
2024-06-25 | 2024-07-04 | EH | 2024-07-17 | 5 | 15 | 1.28 | 8.03 | 0.82 | 7.3 | 490 | 2.5
50 percentile |  |  |  | 4.5 | 9 |  | 6.84 | 0.2995
80 percentile | [9 empty] | 310
90 percentile |  |  |  | 5 | 13.2 | 1.763 | 7.799 | 0.6871
100 percentile | [8 empty] | 7.3
Licence Target
50 percentile |  |  |  | 5 | 10 |  | 7.5 | 0.3
80 percentile | [9 empty] | 200
90 percentile |  |  |  | 10 | 15 | 2 | 10 | 0.5
100 percentile | [8 empty] | 6.5-8.5
*Oil & Grease - Only requires 6 samples per year (Feb, Apr, Jun, Aug, Oct & Dec)
Exceedance Report
Date | Parameter |  | Comment
2024-06-25 | Faecal coliforms & Total phosphorus |  | Backlog of high flows (>7ML/d) still being processed through the plant after 7 June 2024 wet weather event.