## Berrima Website Report
BERRIMA SEWAGE TREATMENT SYSTEM
LICENCE NUMBER 3575
Licencing Period 1 May 2024 - 30 April 2025
FINAL EFFLUENT MONITORING MONTHLY TEST RESULTS (POINT 2)
SAMPLE DATE |  |  |  | BOD | TSS | Ammonia | Total N | Total P | pH | Faecal coliforms | *Oil & Grease
Taken | Received | Reviewed By | Published | (mg/L) | (mg/L) | (mg/L) N | TKN+NOX (mg/L) | (mg/L) | pH units | (CFU/100mL) | (mg/L)
2024-05-28 | 2024-06-06 | WM | 2024-06-14 | 1 | 3 | 0.34 | 4.22 | 0.082 | 7.9 | 120 | NA
2024-06-25 | 2024-07-04 | EH | 2024-07-17 | 1 | 1 | 0.23 | 6.07 | 0.12 | 8 | 55 | 2.5
|  |  |  | 1 | 2 | 0.09 | 6.35 | 0.134 | 7.3 | 76
50 percentile |  |  |  | 1 | 2 |  | 6.07 | 0.12
80 percentile
90 percentile |  |  |  | 1 | 2.8 | 0.318 | 6.294 | 0.1312
100 percentile | [8 empty] | 7.42
Licence Target
50 percentile |  |  |  | 7 | 15 |  | 7 | 0.5
80 percentile
90 percentile |  |  |  | 10 | 20 | 2 | 10 | 1
100 percentile | [8 empty] | 6.5-8.5
*Oil & Grease - Only requires 6 samples per year (Feb, Apr, Jun, Aug, Oct & Dec)
Exceedance Report
Date | Parameter |  | Comment