## Bundanoon Website Report
BUNDANOON SEWAGE TREATMENT SYSTEM
LICENCE NUMBER 2436
Licencing Period 1 May 2024 - 30 April 2025
FINAL EFFLUENT MONITORING FORTNIGHTLY TEST RESULTS (POINT 2)
SAMPLE ANALYSIS DATE |  |  |  | BOD | TSS | Ammonia | Total N | Total P | pH | Faecal coliforms | *Oil & Grease
Taken | Received | Reviewed By | Published | (mg/L) | (mg/L) | (mg/L) N | TKN+NOX | (mg/L) P | pH units | (CFU/100mL) | (mg/L)
2024-05-14 | 2024-05-23 | EH | 2024-06-04 | 1 | 14 | 0.1 | 2.04 | 0.075 | 6.8 | 1 | NA
2024-05-28 | 2024-06-06 | WM | 2024-06-14 | 1 | 3 | 0.11 | 4.68 | 0.074 | 6.9 | 1 | NA
2024-06-11 | 2024-06-22 | EH | 2024-06-28 | 1 | 2 | 0.49 | 4.07 | 0.075 | 6.8 | 1 | NA
2024-06-25 | 2024-07-04 | EH | 2024-07-17 | 1 | 1 | 0.35 | 4.6 | 0.085 | 7.1 | 1 | 2.5
50 percentile |  |  |  | 1 | 2.5 |  | 4.335 | 0.075
80 percentile | [9 empty] | 1
90 percentile |  |  |  | 1 | 10.7 | 0.448 | 4.656 | 0.082
100 percentile | [8 empty] | 7.1
Licence Target
50 percentile |  |  |  | 7 | 10 |  | 6 | 0.2
80 percentile | [9 empty] | 200
90 percentile |  |  |  | 10 | 15 | 2 | 10 | 0.3
100 percentile | [8 empty] | 6.5-8.5
*Oil & Grease - Only requires 6 samples per year (Feb, Apr, Jun, Aug, Oct & Dec)
Exceedance Report
Date | Parameter |  | Comment