## Moss Vale EPL 1731 Report
MOSS VALE SEWAGE TREATMENT SYSTEM
LICENCE NUMBER 1731
Licencing Period 1 May 2024 - 30 April 2025
FINAL EFFLUENT MONITORING FORTNIGHTLY TEST RESULTS (POINT 1)
SAMPLE DATE |  |  |  | BOD | TSS | Ammonia | Total N | Total P | pH | Faecal coliforms | *Oil & Grease
Taken | Received | Reviewed by | Published | (mg/L) | (mg/L) | (mg/L) N | TKN+NOX | (mg/L) P | pH units | (CFU/100mL) | (mg/L)
2024-05-14 | 2024-05-23 | EH | 2024-06-04 | 1 | 3 | 0.22 | 4.26 | 0.331 | 7 | 880 | NA
2024-05-28 | 2024-06-06 | WM | 2024-06-14 | 1 | 3 | 0.61 | 6.24 | 0.275 | 7.2 | 8 | NA
2024-06-11 | 2024-06-22 | EH | 2024-06-28 | 1 | 1 | 0.35 | 6.79 | 0.492 | 7 | 2600 | NA
2024-06-25 | 2024-07-04 | EH | 2024-07-17 | 1 | 2 | 1.29 | 6.22 | 0.33 | 7.1 | 270 | NA
50 percentile |  |  |  | 1 | 2.5 |  | 6.23 | 0.3305
80 percentile | [9 empty] | 1568
90 percentile |  |  |  | 1 | 3 | 1.086 | 6.625 | 0.4437
100 percentile | [8 empty] | 7.2
Licence Target
50 percentile |  |  |  | 7 | 10 |  | 7 | 0.5
80 percentile | [9 empty] | 200
90 percentile |  |  |  | 10 | 15 | 2 | 10 | 1
100 percentile | [8 empty] | 6.5-8.5
*Oil & Grease - Only requires 6 samples per year (Feb, Apr, Jun, Aug, Oct & Dec)
Exceedance Report
Date | Parameter |  | Comment
2024-05-14 | Faecal coliforms |  | High rainfall prior to testing date, approx 128mm.
2024-06-11 | Faecal coliforms |  | High rainfall prior to testing date, approx 153mm.
2024-06-25 | Faecal coliforms |  | Still processing high flow rates through UV system, from wet weather event. UV system has been cleaned and serviced.